## Slide 1: Baglung Nagar Water Supply and Sanitation Project
Project Appraisal
Group work

## Slide 2: Group Members
Kanchan Kumar Nayak
Lok Bahadur Bhandari
Purna Prasad Upadhyaya
Ram Sogarath Sah
Roshan Neupane
Rupak Maharjan

## Slide 3: Project Area - Introduction
Name of Project: Baglung Nagar Water Supply and Sanitation Project (WSSP)
District: Baglung
Municipality: Baglung
Ward No.: 1,2,3
(Baglung Bazaar Area)
Population : 30300 (2017)
Household: 5050 (2017)

## Slide 4: Existing Features of Baglung WSP
Total Household | 5050
Total Population | 30300
Household Connection | 3596
No. of water sources | 3 nos
Capacity of Sources of water | 36.5 liter per second (31 lps in dry season)
Capacity of Treatment Plant | 60 to 65 lps
Capacity of RVT | 10,00,000 liter
Operation and Management | Baglung Nagar Water Users Committee

## Slide 5: Existing Water Supply Plant

## Slide 6: Layout Plan of Existing WSP

## Slide 7: Objective of Feasibility Study
To upgrade existing water supply system of Baglung urban area by adding new sources to fulfill water demand and expand distribution system to new demand areas.

## Slide 8: Proposed Features
Name of sources | Kathekhola- Gaudakot source
Design Discharge | 28 lps by new source
Design Population | 41595 nos
Design Period | 15 year
Transmission System | Lift system by pumping 300m uplift head
New structures | Intake at source, Pumping system, office and guard building, extension of distribution system
Approach road and Distance | Baglung Bazaar to Gaudakot- Simle Road (300m downhill from existing water supply treatment Plant at Ratmata)
Estimated Cost | NRs. 9,13,88,700.00 (70%- Gov. and 30%- User)
Construction materials | Pipes, fittings, water pump, cement, sand, aggregate, steel reinforcement, pumping system

## Slide 9: Demand Analysis
Item | Base Year (2018) | Design year (2033)
Population | 30906 | 41595
Per Capita Demand | 100 lpcd | 100 lpcd
Total Water Demand | 39.35 lps | 58.84lps
Existing Water Supply | 36.5 lps (31 lps at Dry months) | 
Demand deficit | 8.35 lps | 27.84 lps

## Slide 10: Technical Analysis
Available Sources:
          Dundiya Khola ( 130-150 lps, Social conflict )
          Kaligandaki River ( unlimited discharge, Black water, High investment cost, double stage lift)
          Kathekhola Gaudakot ( 130- 150 lps, 250m head, feasible source)
Design Parameter:
  Sump well at Kathekhola
  Total Head - 223m ( Single Stage pumping)
  Sump well to Treatment Plant Distance - 350m
  Pump capacity - 60 HP
  Operational Time – 24 hr
  Pumping Rate – 14 lps
  Diesel Generator – 1 no.
  Transformer 100 KVA – 1 no.

## Slide 11: Technical Analysis
Operation Technology :
  Skilled Manpower
        Engineer/ Manager - 1no.
        Plant Supervisor/ Mechanical Overseer - 1 no.
        Pump Operator - 2 no.
        Plumber - 1 no.
  Maintenance cost - NRs. 6,85,415.00
  Operational cost - NRs. 75,17,260.00

## Slide 12: Financial Analysis
Investment cost : NRs. 9,13,88,750.00
- Government – NRs. 6,39,72,125.00
(70% of Total Cost)
- Users - NRs. 2,74,16,625.00
( Cash 10%, kind contribution 20% of Total Cost)
Willingness and commitment of investment from WUSC
  Maintenance cost - NRs. 6,85,415.00
  Operational cost - NRs. 75,17,260.00

## Slide 13: Financial Analysis contd….
Affordability
  Income from New Connection- NRs. 21,010.00 (5000 refundable)
  Tariff per Month per HH – NRs. 218.00
  Tariff per Year – 218*12*5151= NRs. 1,34,75,016.00
Total Cash inflow: NRs. 1,34,75,016.00
Total cash outflow: NRs. 82,02,675.00

## Slide 14: Environmental Aspect
Population of Project Service area- 41,595 nos.
Threshold less than 10,000- 1,00,000 nos. population as per EPA& EPR Initial Environment Examination (IEE) is required

## Slide 15: Conclusion
Technically and Financially feasible
Requirement of conducting IEE

## Slide 16: Conclusion and Recommendation
Water tariff is high for new connection in comparison to present HH connection
Population analysis of base year is not realistic
Objective is not specific on report
Remuneration is under estimate specially lower staff
Risk analysis of project is not carried ( extra pump)
Institutional linkage with user group/government agencies
Monitoring plan of water quality testing should be made

## Slide 17: Thank You